## Main
Thermal Calculation for Steam Surface Condenser
AP Engineering Serivces
C-11, Jeevan Vihar, Ghaziabad - 201002
M +917042102575
M +918004926736
apengineeringservices@writeme.com
apengineeringservicesgzb@gmail.com
pavansrivastavapower@gmail.com
srivastavas2003@gmail.com
srivastavas2003@yahoo.co.in

## INPUT
PROJECT NAME
XXXXXXXXXXXX
Input Data For Condenser
1 | Steam flow to condenser | 30100 | Kg/Hr
2 | Exhaust Pressure | 0.095 | Ata
3 | Inlet enthalpy to Condenser | 1010 | BTU/lb
4 | Temperature at Exhaust Exit | 112.01 | °F
5 | Cooling water inlet temperature | 32 | °C
6 | Cooling water outlet temperature | 40 | °C
7 | Cleanliness Factor | 0.85
8 | Water Velocity | 6 | Ft/sec | * Refer table for Material Code
9 | Tube Material & Gague * | AB18 |  | Admiralty Metal | AB
10 | Outside diameter of tube | 0.75 | inch | Arsenical Copper | AC
11 | Tube gauge | 18 |  | Copper Iron 194 | CI
12 | GVC Data |  |  | Aluminum Brass | ABR
12a | Flow | 300 | kg/hr | 90-10 Cu-Ni | CN90
12b | Temp of condensate outlet | 99.35 | °C | 70-30- Cu-Ni | CN70
13 | Ejector Data |  |  | Colled Rolled Carbon Steel | CS
13a | inter condenser return water flow | 175 | kg/hr | Stainless Steel Type 304/316 | SS
13b | inter condenser return water temp. | 73.2 | °C | Titanium | T
13c | After condenser return water flow | 64.63 | Kg/Hr | UNS N08367 | U1
13d | After condenser return water temp. | 85 | °C | UNS S430.35 | U2
14 | Steam No of Pass | 1 |  | UNS S44735 | U3
15 | Water No of Pass | 2
16 | Tube plugging margin in persentage | 10 | %
17 | Extra surface area in length | 10 | %
| Prepared By | Pavan Srivastava
Password for editing input data (in Red) - 123

## specification
SPECIFICATION SHEET (Condenser)
PROJECT |  | XXXXXXXXXXXX
| SL. NO. | DESCRIPTION | UNITS | Shell Side | Tube Side
Design Data
| A | Desing pressure | kg/cm²g | 1.1 & full Vacumn | 3
| B | Desing temperature | °C | 120 | 60
| C | Operating pressure | kg/cm²g | 0.09 | ---
| D | Operating Temperature (inlet) | °C | 44.0111 | 32
| E | Operating Temperature (outlet) | °C |  | 40
| F | Hydro test pressure | kg/cm²g | 1.65 | 4.5
| G | Fluid Circulated |  | Steam | Water
| H | Steam Quantity | Kg/hr | 30100 | ---
| I | Number of pass |  | 1 | 2
| J | Joint efficiency | % | 85 | 85
| K | Corrosion allowance | mm | 1.6 | 3
| L | Tube size & gauge |  | 0.75 | 18
| M | Tube Material | % | Admiralty Metal
| N | No of Tube |  | 3038.7324
| N | Length of tube | M | 4.4814
| O | Hot Well Capacity(retention time) | min | 3
| P | Surface are required/provided | M² | 734.8347 | 808.3182
| Q | Condenser heat load | Kcal/kg | 15570944.7722
| R | Auxilary heat load | Kcal/kg | 24358.8341
| S | Total Heat Load | Kcal/kg | 15595303.6063
| T | Cooling water requirement | M3/hr | 1958.8262
| U | Cleanliness factor |  | 0.85
| V | Water Velocity Loss | kg/cm²g | 0.38143
Notes:-
|  | Name | Signature |  | Date
| Pprepared by | Pavan Srivastava
| Checked by | 0

## calculation
SURFACE CONDENSER
XXXXXXXXXXXX
steam flow to condenser |  |  | Kg/hr | 30100
Exhaust Pressure |  |  | ata | 0.095
Condenser Pressure (consider 0.005 ata Pressure drop) |  |  | ata | 0.09
|  | Vacumn | In Hg | 2.6929
Inlet enthalpy to condenser (from steam path calculation) |  |  | BTU/lb | 1010
|  | multiply by 2.204 | BTU/Kg | 2226.04
|  | multiply by 252.116( 1 BTU= 252.16 Cal) | Cal/kg | 561318.2464
|  | devide by 1000 (H steam) | Kcal/kg | 561.3182
Temperature at exhaust exist (from calculation sheet) |  |  | °F | 112.01
|  |  | °C | 44.45
Temperature at | 2.69 | from HEI Appendix D (Properties of steam) | °F | 111.22
|  | H condensate (Ts) | °C | 44.0111
Cooling water inlet temperature (T1) |  |  | °F | 89.6
Cooling water outlet temperature (T2) |  |  | °F | 104
Cleanliness factor |  |  |  | 0.85
Water velocity (Vw) |  |  | ft/sec | 6
|  |  | M/sec | 1.8288
tube details
|  | Tube outside diameter | inch | 0.75
|  | Material & Gauge |  | AB18
Heat Load Calculation (from HEI 4.2)
Auxiliary heat load calculation
| GVC Load | (refer GVC calculation)
| Temperature of condensate outlet |  | °C | 99.35
| flow rate |  | kg/hr | 300
| heat load = condensate outlet temp-condensate temp) x flow |  | kcal/hr | 16601.6667
Ejector load calculation (refer Ejector calculation)
Inter condenser
|  | Condenser drain temp. | °C | 73.2
|  | Flow | kg/hr | 175
| Heat Load = Inter. Condenser drain temp-condensate temp)* flow |  | Kcal/kg | 5108.0556
After conderser
|  | Condenser drain temp. | °C | 85
|  | Flow | kg/hr | 64.63
| Hear load = after condenser drain temp-condensate temp)*flow |  | Kcal/kg | 2649.1119
| Total Ejector Load = inter condser + after conderser load |  | kcal/kg | 7757.1674
| Total Auxiliary Heat Load = GVC load + Ejector Load |  | Kcal/kg | 24358.8341
| Heat load on conderser = (H steam - H condensate)xWs |  | Kcal/kg | 15570944.7722
| Total heat load = condeser load + auxiliary load |  | Kcal/kg | 15595303.6063
Heat Transfer rate Calculation (HEI 4.2.1)
U = U1 x Fw x Fm x Fc
|  | U1 = uncorrected Heat transfer coefficient | Btu/hr*ft2*°F | 654
(Fig.1 or table 1 of HEI page No.7)
|  | Fw= Inlet water temperature correction factor |  | 1.072
( Fig.2 or table 2 of HEI page No.9)
|  | Fm = Tube material and gauge correction factor |  | 1
( Table 3 of HEI page No.11)
|  | Fc = Cleanliness Factor consider 0.85 |  | 0.85
|  | Corrected heat transfer correction factor | Btu/hr*ft2*°F | 595.9248
|  | for kcal/Hr*M2*°C multiply by 4.882428 | kcal/hr*m2*°C | 2909.5599
LMTD Calculation
TR
LMDT = ---------------------
( I Td )
Ln(---------)
( T Td )
|  | TR = T2 - T1 | °C | 8
|  | I Td = Ts - T1 | °C | 12.0111
|  | T Td = Ts - T2 | °C | 4.0111
|  | Ln |  | 1.0968
|  | LMTD |  | 7.2942
Surface Area Calculation
Q = U x As X LMTD
|  | As = | M2 | 734.8347
|  | Add margin in length |  | 808.3182
Water Quantity Calculation (ref HEI 4.1.4)
Q
|  | W = ---------------------------------------- | M3/Hr | 1958.8262
Sg x Cp x Tr
|  | Sg = Specific gravity |  | 993.64
|  | Cp = specific Heat |  | 1
|  | Tr = Temperature rise of water |  | 8
No. of Tube Calculation
Inside Area tube (ref HEI table 7)
|  | Inside dia | inch | 0.652
|  | Area | M2 | 0.0002154
Flow in M/sec
| No. of Tube = ---------------------------------------- |  | Nos | 1381.242
Area x Velocity
| No. of tube with plugging margin per pass |  |  | 1519.3662
| Total No of tube = No of tube per pass x no of pass |  |  | 3038.7324
Length of tube calculation
| Tube Surface Area |  | M2 | 0.059358
Required surface area
| Length of tube = ------------------------------------------------- |  | M | 4.4814
Tube Area x No of tube
| With marign in surface area tube length |  | M | 4.4814
(INCLUDING AREA OF PLUGGING MARGIN)
|  |  | ft | 14.7027
Circulating Water Pressure Loss
The circulating water pressure loss through the condenser is calculated
using the following equations.
Rtt = Lt ( Rt x R2 x R1) + Sigma Re
|  | Sigme Re | ft of water | 3.12
|  | Rtt = Total Loss | ft of water | 11.626
|  |  | M of Water | 3.8143
|  |  | Kg/cm²g | 0.38143
|  | Lt = Tube Length x Number of Pass |  | 29.4054
|  | R1 = Temperature Correction for friction loss in tubes. |  | 1.1476
1.75
|  | 0.00642 x( Vw ) | 0.14767
|  | R2 x Rt = ------------------------------------------ | ------------------- | 0.25205
|  | 1.25 | 0.58588
( Dl )
R2 = Gauge correction factor for friction loss
Rt = Tube friction loss (ft of water / ft of length)
|  | Vw = Water Velocity | ft/sec | 6
|  | Di = Tube inside diameter |  | 0.652

## U1
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
| Tube Size | [7 empty] | TUBE VELOCITY IN Ft/sce
1 | TO | 1 | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12
2 | 0.625 | 2 | 462.5 | 499.5 | 534 | 566.4 | 597 | 626.2 | 654 | 680.7 | 706.4 | 731.2 | 755.2 | 775.5 | 795.3 | 814.1 | 931.9 | 848.9 | 865.2 | 880.7 | 895.6
3 | 0.75 | 3 | 462.5 | 499.5 | 534 | 566.4 | 597 | 626.2 | 654 | 680.7 | 706.4 | 731.2 | 755.2 | 775.5 | 795.3 | 814.1 | 931.9 | 848.9 | 865.2 | 880.7 | 895.6
4 | 0.875 | 4 | 455 | 492 | 526 | 557.9 | 588.14 | 616.8 | 644.2 | 670.5 | 695.8 | 720.3 | 743.9 | 763.9 | 783.2 | 801.6 | 819 | 835.6 | 851.5 | 866.6 | 881.1
5 | 1 | 5 | 455 | 492 | 526 | 557.9 | 588.14 | 616.8 | 644.2 | 670.5 | 695.8 | 720.3 | 743.9 | 763.9 | 783.2 | 801.6 | 819 | 835.6 | 851.5 | 866.6 | 881.1
6 | 1.125 | 6 | 448.6 | 484.5 | 518 | 549.4 | 579.1 | 607.4 | 634.4 | 660.3 | 685.2 | 709.3 | 732.6 | 752 | 770.7 | 788.4 | 805.3 | 821.4 | 836.7 | 851.3 | 865.3
7 | 1.25 | 7 | 448.6 | 484.5 | 518 | 549.4 | 579.1 | 607.4 | 634.4 | 660.3 | 685.2 | 709.3 | 732.6 | 752 | 770.7 | 788.4 | 805.3 | 821.4 | 836.7 | 851.3 | 865.3
8 | 1.375 | 8 | 441.7 | 477.1 | 510 | 540.9 | 570.2 | 598 | 624 | 650.1 | 674.7 | 698.3 | 721.2 | 740.4 | 758.7 | 776.1 | 792.6 | 808.3 | 823.2 | 837.5 | 851.2
9 | 1.5 | 9 | 441.7 | 477.1 | 510 | 540.9 | 570.2 | 598 | 624 | 650.1 | 674.7 | 698.3 | 721.2 | 740.4 | 758.7 | 776.1 | 792.6 | 808.3 | 823.2 | 837.5 | 851.2
10 | 1.625 | 10 | 434.7 | 469.6 | 502 | 532.5 | 561.3 | 588.6 | 614.8 | 639.9 | 664.1 | 687.4 | 709.9 | 727.8 | 745.7 | 762.7 | 778.8 | 794.1 | 808.8 | 822.7 | 836
11 | 1.75 | 11 | 434.7 | 469.6 | 502 | 532.5 | 561.3 | 588.6 | 614.8 | 639.9 | 664.1 | 687.4 | 709.9 | 727.8 | 745.7 | 762.7 | 778.8 | 794.1 | 808.8 | 822.7 | 836
12 | 1.875 | 12 | 427.8 | 462.1 | 494 | 524 | 552.3 | 579.8 | 605 | 629.7 | 653.5 | 676.4 | 698.6 | 716.8 | 734.4 | 751 | 766.8 | 781.8 | 796.2 | 809.8 | 822.9
13 | 2 | 13 | 427.8 | 462.1 | 494 | 524 | 552.3 | 579.8 | 605 | 629.7 | 653.5 | 676.4 | 698.6 | 716.8 | 734.4 | 751 | 766.8 | 781.8 | 796.2 | 809.8 | 822.9
| Tube OD | 0.75 | 6
| Water Velocity | 6
3
| U (uncorrected) | 654

## Fw
1 | 2
INLET WATER TEMPERATURE
CORRECTION FACTOR
Fw
INLET WATER °F | Fw
30 | 0.65
31 | 0.659
32 | 0.669
33 | 0.678
34 | 0.687
35 | 0.696
36 | 0.706
37 | 0.715
38 | 0.724
39 | 0.733
40 | 0.743
41 | 0.752
42 | 0.761
43 | 0.77
44 | 0.78
45 | 0.789
46 | 0.798
47 | 0.807
48 | 0.816
49 | 0.825
50 | 0.834
51 | 0.843
52 | 0.852
53 | 0.861
54 | 0.87
55 | 0.879
56 | 0.888
57 | 0.897
58 | 0.905
59 | 0.914
60 | 0.923
61 | 0.932
62 | 0.941
63 | 0.95
64 | 0.959
65 | 0.968
66 | 0.975
67 | 0.982
68 | 0.989
69 | 0.994
70 | 1
71 | 1.005
72 | 1.01
73 | 1.015
74 | 1.02
75 | 1.025
76 | 1.029
77 | 1.033
78 | 1.037
79 | 1.041
80 | 1.045
81 | 1.048
82 | 1.051
83 | 1.054
84 | 1.057
85 | 1.06
86 | 1.063
87 | 1.066
88 | 1.069
89 | 1.072
90 | 1.075
91 | 1.078
92 | 1.08
93 | 1.083
94 | 1.085
95 | 1.088
96 | 1.09
97 | 1.092
98 | 1.095
99 | 1.097
100 | 1.1
101 | 1.103
102 | 1.105
103 | 1.108
104 | 1.11
105 | 1.113
106 | 1.115
107 | 1.117
108 | 1.119
109 | 1.121
110 | 1.123
111 | 1.125
112 | 1.127
113 | 1.129
114 | 1.131
115 | 1.133
116 | 1.135
117 | 1.137
118 | 1.139
119 | 1.141
120 | 1.143

## Fm
1 | 2 | 3 | 4
TUBE MATERIAL AND GAUGE CORRECTION FACTOR Fm
CODE | TUBE WALL GAUGE - BWG | Fw | TUBE MATERIAL
AB25 | 25 | 1.03 | Admiralty Metal | Admiralty Metal | AB
AB24 | 24 | 1.03 | Admiralty Metal | Arsenical Copper | AC
AB23 | 23 | 1.02 | Admiralty Metal | Copper Iron 194 | CI
AB22 | 22 | 1.02 | Admiralty Metal | Aluminum Brass | ABR
AB20 | 20 | 1.01 | Admiralty Metal | 90-10 Cu-Ni | CN90
AB18 | 18 | 1 | Admiralty Metal | 70-30- Cu-Ni | CN70
AB16 | 16 | 0.98 | Admiralty Metal | Colled Rolled Carbon Steel | CS
AB14 | 14 | 0.96 | Admiralty Metal | Stainless Steel Type 304/316 | SS
AB12 | 12 | 0.93 | Admiralty Metal | Titanium | T
AC25 | 25 | 1.04 | Arsenical Copper | UNS N08367 | U1
AC24 | 24 | 1.04 | Arsenical Copper | UNS S430.35 | U2
AC23 | 23 | 1.04 | Arsenical Copper | UNS S44735 | U3
AC22 | 22 | 1.03 | Arsenical Copper | UNS S44660 | U4
AC20 | 20 | 1.03 | Arsenical Copper
AC18 | 18 | 1.02 | Arsenical Copper
AC16 | 16 | 1.01 | Arsenical Copper
AC14 | 14 | 1 | Arsenical Copper
AC12 | 12 | 0.98 | Arsenical Copper
CI25 | 25 | 1.04 | Copper Iron 194
CI24 | 24 | 1.04 | Copper Iron 194
CI23 | 23 | 1.04 | Copper Iron 194
CI22 | 22 | 1.04 | Copper Iron 194
CI20 | 20 | 1.03 | Copper Iron 194
CI18 | 18 | 1.03 | Copper Iron 194
CI16 | 16 | 1.02 | Copper Iron 194
CI14 | 14 | 1.01 | Copper Iron 194
CI12 | 12 | 1 | Copper Iron 194
ABR25 | 25 | 1.03 | Aluminum Brass
ABR24 | 24 | 1.02 | Aluminum Brass
ABR23 | 23 | 1.02 | Aluminum Brass
ABR22 | 22 | 1.02 | Aluminum Brass
ABR20 | 20 | 1.01 | Aluminum Brass
ABR18 | 18 | 0.99 | Aluminum Brass
ABR16 | 16 | 0.97 | Aluminum Brass
ABR14 | 14 | 0.95 | Aluminum Brass
ABR12 | 12 | 0.92 | Aluminum Brass
ABZ25 | 25 | 1.02 | Aluminum Bronze
ABZ24 | 24 | 1.02 | Aluminum Bronze
ABZ23 | 23 | 1.01 | Aluminum Bronze
ABZ22 | 22 | 1.01 | Aluminum Bronze
ABZ20 | 20 | 1 | Aluminum Bronze
ABZ18 | 18 | 0.98 | Aluminum Bronze
ABZ16 | 16 | 0.96 | Aluminum Bronze
ABZ14 | 14 | 0.93 | Aluminum Bronze
ABZ12 | 12 | 0.89 | Aluminum Bronze
CN9025 | 25 | 1 | 90-10 Cu-Ni
CN9024 | 24 | 0.99 | 90-10 Cu-Ni
CN9023 | 23 | 0.99 | 90-10 Cu-Ni
CN9022 | 22 | 0.98 | 90-10 Cu-Ni
CN9020 | 20 | 0.96 | 90-10 Cu-Ni
CN9018 | 18 | 0.93 | 90-10 Cu-Ni
CN9016 | 16 | 0.89 | 90-10 Cu-Ni
CN9014 | 14 | 0.85 | 90-10 Cu-Ni
CN9012 | 12 | 0.8 | 90-10 Cu-Ni
CN7025 | 25 | 0.97 | 70-30- Cu-Ni
CN7024 | 24 | 0.97 | 70-30- Cu-Ni
CN7023 | 23 | 0.96 | 70-30- Cu-Ni
CN7022 | 22 | 0.95 | 70-30- Cu-Ni
CN7020 | 20 | 0.92 | 70-30- Cu-Ni
CN7018 | 18 | 0.88 | 70-30- Cu-Ni
CN7016 | 16 | 0.83 | 70-30- Cu-Ni
CN7014 | 14 | 0.78 | 70-30- Cu-Ni
CN7012 | 12 | 0.71 | 70-30- Cu-Ni
CS25 | 25 | 1 | Colled Rolled Carbon Steel
CS24 | 24 | 1 | Colled Rolled Carbon Steel
CS23 | 23 | 0.99 | Colled Rolled Carbon Steel
CS22 | 22 | 0.98 | Colled Rolled Carbon Steel
CS20 | 20 | 0.97 | Colled Rolled Carbon Steel
CS18 | 18 | 0.93 | Colled Rolled Carbon Steel
CS16 | 16 | 0.89 | Colled Rolled Carbon Steel
CS14 | 14 | 0.85 | Colled Rolled Carbon Steel
CS12 | 12 | 0.8 | Colled Rolled Carbon Steel
SS25 | 25 | 0.91 | Stainless Steel Type 304/316
SS24 | 24 | 0.9 | Stainless Steel Type 304/316
SS23 | 23 | 0.88 | Stainless Steel Type 304/316
SS22 | 22 | 0.86 | Stainless Steel Type 304/316
SS20 | 20 | 0.82 | Stainless Steel Type 304/316
SS18 | 18 | 0.75 | Stainless Steel Type 304/316
SS16 | 16 | 0.69 | Stainless Steel Type 304/316
SS14 | 14 | 0.62 | Stainless Steel Type 304/316
SS12 | 12 | 0.54 | Stainless Steel Type 304/316
T25 | 25 | 0.95 | Titanium
T24 | 24 | 0.94 | Titanium
T23 | 23 | 0.92 | Titanium
T22 | 22 | 0.91 | Titanium
T20 | 20 | 0.88 | Titanium
T18 | 18 | 0.82 | Titanium
T16 | 16 | 0.77 | Titanium
T14 | 14 | 0.71 | Titanium
T12 | 12 | 0.63 | Titanium
U125 | 25 | 0.9 | UNS N08367
U124 | 24 | 0.89 | UNS N08367
U123 | 23 | 0.87 | UNS N08367
U122 | 22 | 0.85 | UNS N08367
U120 | 20 | 0.81 | UNS N08367
U118 | 18 | 0.74 | UNS N08367
U116 | 16 | 0.67 | UNS N08367
U114 | 14 | 0.6 | UNS N08367
U112 | 12 | 0.52 | UNS N08367
U225 | 25 | 0.95 | UNS S430.35
U224 | 24 | 0.94 | UNS S430.35
U223 | 23 | 0.92 | UNS S430.35
U222 | 22 | 0.91 | UNS S430.35
U220 | 20 | 0.88 | UNS S430.35
U218 | 18 | 0.82 | UNS S430.35
U216 | 16 | 0.77 | UNS S430.35
U214 | 14 | 0.71 | UNS S430.35
U212 | 12 | 0.63 | UNS S430.35
U225 | 25 | 0.93 | UNS S44735
U224 | 24 | 0.91 | UNS S44735
U223 | 23 | 0.9 | UNS S44735
U222 | 22 | 0.88 | UNS S44735
U220 | 20 | 0.85 | UNS S44735
U218 | 18 | 0.78 | UNS S44735
U216 | 16 | 0.72 | UNS S44735
U214 | 14 | 0.65 | UNS S44735
U212 | 12 | 0.57 | UNS S44735
U325 | 25 | 0.93 | UNS S44660
U324 | 24 | 0.91 | UNS S44660
U323 | 23 | 0.9 | UNS S44660
U322 | 22 | 0.88 | UNS S44660
U320 | 20 | 0.85 | UNS S44660
U318 | 18 | 0.78 | UNS S44660
U316 | 16 | 0.72 | UNS S44660
U314 | 14 | 0.65 | UNS S44660
U312 | 12 | 0.57 | UNS S44660

## tube
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
TUBE INSIDE DIAMETER
1 | TUBE OD | TUBE GAUGE | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
2 | 0.625 | 2 | 0.107 | 0.135 | 0.157 | 0.185 | 0.209 | 0.231 | 0.245 | 0.259 | 0.277 | 0.291 | 0.305 | 0.311 | 0.319 | 0.325 | 0.331 | 0.335
3 | 0.5 | 3 | 0.232 | 0.26 | 0.282 | 0.31 | 0.334 | 0.356 | 0.37 | 0.384 | 0.402 | 0.416 | 0.43 | 0.436 | 0.444 | 0.45 | 0.456 | 0.46
4 | 0.375 | 4 | 0.357 | 0.385 | 0.407 | 0.435 | 0.459 | 0.481 | 0.495 | 0.509 | 0.527 | 0.541 | 0.555 | 0.561 | 0.569 | 0.575 | 0.581 | 0.585
5 | 0.75 | 5 | 0.482 | 0.515 | 0.532 | 0.56 | 0.584 | 0.606 | 0.62 | 0.634 | 0.652 | 0.666 | 0.68 | 0.686 | 0.694 | 0.7 | 0.706 | 0.71
6 | 0.875 | 6 | 0.607 | 0.635 | 0.657 | 0.685 | 0.709 | 0.731 | 0.745 | 0.759 | 0.777 | 0.791 | 0.805 | 0.811 | 0.819 | 0.825 | 0.831 | 0.835
7 | 1 | 7 | 0.732 | 0.76 | 0.782 | 0.81 | 0.834 | 0.856 | 0.87 | 0.884 | 0.902 | 0.916 | 0.93 | 0.936 | 0.944 | 0.95 | 0.956 | 0.96
8 | 1.125 | 8 | 0.857 | 0.885 | 0.907 | 0.935 | 0.959 | 0.981 | 0.995 | 1.009 | 1.027 | 1.041 | 1.005 | 1.061 | 1.069 | 1.075 | 1.081 | 1.085
9 | 1.25 | 9 | 0.982 | 1.01 | 1.032 | 1.06 | 1.084 | 1.106 | 1.12 | 1.134 | 1.152 | 1.166 | 1.18 | 1.186 | 1.194 | 1.2 | 1.206 | 1.21
10 | 1.5 | 10 | 1.232 | 1.26 | 1.282 | 1.31 | 1.334 | 1.356 | 1.37 | 1.384 | 1.402 | 1.416 | 1.43 | 1.436 | 1.444 | 1.45 | 1.456 | 1.46
11 | 2 | 11 | 1.732 | 1.76 | 1.782 | 1.781 | 1.834 | 1.856 | 1.87 | 1.884 | 1.902 | 1.916 | 1.93 | 1.936 | 1.944 | 1.95 | 1.956 | 1.96
| Tube Outside dia |  | 11: 0.75
| Tube Gauge |  | 11: 18
| Tube Outside dia gauge |  | 11: 5
| Tube inside diameter |  | 11: 0.652

## STEAM
1 | 2 | 3
PROPERTIES OF SATURATED STEAM
Absolute | Temperature | Sp Vol.
pressure in Hg | °F | cu ft / lb
0.5 | 58.81 | 1256.95
0.51 | 59.37 | 1233.61
0.52 | 59.91 | 1211.14
0.53 | 60.45 | 1189.49
0.54 | 60.97 | 1168.63
0.55 | 61.49 | 1148.51
0.56 | 62 | 1129.09
0.57 | 62.5 | 1110.34
0.58 | 63 | 1092.21
0.59 | 63.49 | 1074.69
0.6 | 63.96 | 1057.73
0.61 | 64.44 | 1041.32
0.62 | 64.9 | 1025.42
0.63 | 65.39 | 1010.02
0.64 | 65.82 | 995.08
0.65 | 66.26 | 980.59
0.66 | 66.7 | 966.53
0.67 | 67.14 | 952.88
0.68 | 67.57 | 939.62
0.69 | 67.99 | 926.74
0.7 | 68.41 | 914.21
0.71 | 68.82 | 902.03
0.72 | 69.23 | 890.18
0.73 | 69.64 | 878.65
0.74 | 70.03 | 867.41
0.75 | 70.43 | 856.48
0.76 | 70.82 | 845.82
0.77 | 71.2 | 835.43
0.78 | 71.58 | 825.3
0.79 | 71.96 | 815.42
0.8 | 72.33 | 805.78
0.81 | 72.7 | 796.38
0.82 | 73.06 | 787.19
0.83 | 73.42 | 778.23
0.84 | 73.78 | 769.47
0.85 | 74.13 | 760.91
0.86 | 74.48 | 752.54
0.87 | 74.83 | 744.37
0.88 | 75.17 | 736.37
0.89 | 75.51 | 728.55
0.9 | 75.84 | 720.9
0.91 | 76.18 | 713.41
0.92 | 76.51 | 706.08
0.93 | 76.83 | 698.91
0.94 | 77.15 | 691.88
0.95 | 77.47 | 685
0.96 | 77.79 | 678.26
0.97 | 78.11 | 671.65
0.98 | 78.42 | 665.17
0.99 | 78.73 | 658.83
1 | 79.03 | 652.6
1.01 | 79.33 | 646.5
1.02 | 79.64 | 640.51
1.03 | 79.93 | 634.63
1.04 | 80.23 | 628.87
1.05 | 80.52 | 623.21
1.06 | 80.81 | 617.66
1.07 | 81.1 | 612.21
1.08 | 81.39 | 606.85
1.09 | 81.67 | 601.59
1.1 | 81.95 | 596.43
1.11 | 82.23 | 591.35
1.12 | 82.51 | 586.37
1.13 | 82.78 | 581.47
1.14 | 83.06 | 576.65
1.15 | 83.33 | 571.91
1.16 | 83.6 | 567.26
1.17 | 83.86 | 562.68
1.18 | 84.13 | 558.18
1.19 | 84.39 | 553.75
1.2 | 84.65 | 549.39
1.21 | 84.91 | 545.11
1.22 | 85.17 | 540.89
1.23 | 85.42 | 536.74
1.24 | 85.68 | 532.65
1.25 | 85.93 | 528.63
1.26 | 86.18 | 524.67
1.27 | 86.43 | 520.77
1.28 | 86.67 | 516.93
1.29 | 86.92 | 513.14
1.3 | 87.16 | 509.42
1.31 | 87.4 | 505.75
1.32 | 87.64 | 502.13
1.33 | 87.88 | 498.57
1.34 | 88.12 | 495.06
1.35 | 88.35 | 491.6
1.36 | 88.59 | 488.19
1.37 | 88.82 | 484.82
1.38 | 89.05 | 481.51
1.39 | 89.28 | 478.24
1.4 | 89.51 | 475.01
1.41 | 89.73 | 471.84
1.42 | 89.96 | 468.7
1.43 | 90.18 | 465.61
1.44 | 90.4 | 462.56
1.45 | 90.63 | 459.55
1.46 | 90.85 | 456.58
1.47 | 91.06 | 453.65
1.48 | 91.28 | 450.76
1.49 | 91.5 | 447.9
1.5 | 91.71 | 445.09
1.51 | 91.93 | 442.3
1.52 | 92.14 | 439.56
1.53 | 92.35 | 436.85
1.54 | 92.56 | 434.17
1.55 | 92.77 | 431.53
1.56 | 92.97 | 428.92
1.57 | 93.18 | 426.35
1.58 | 93.39 | 423.8
1.59 | 93.59 | 421.29
1.6 | 93.79 | 418.8
1.61 | 94 | 416.35
1.62 | 94.2 | 413.93
1.63 | 94.4 | 411.53
1.64 | 94.59 | 409.16
1.65 | 94.79 | 406.83
1.66 | 94.99 | 404.51
1.67 | 95.18 | 402.23
1.68 | 95.38 | 399.97
1.69 | 95.37 | 397.74
1.7 | 95.77 | 395.54
1.71 | 95.96 | 393.35
1.72 | 96.15 | 391.2
1.73 | 96.34 | 389.07
1.74 | 96.53 | 386.96
1.75 | 96.71 | 384.87
1.76 | 96.9 | 382.81
1.77 | 97.09 | 380.77
1.78 | 97.27 | 378.76
1.79 | 97.46 | 376.76
1.8 | 97.64 | 374.79
1.81 | 97.82 | 372.84
1.82 | 98 | 370.9
1.83 | 98.18 | 368.99
1.84 | 98.36 | 367.1
1.85 | 98.54 | 365.23
1.86 | 98.72 | 363.38
1.87 | 98.9 | 361.55
1.88 | 99.07 | 359.74
1.89 | 99.25 | 357.94
1.9 | 99.42 | 356.17
1.91 | 99.6 | 354.41
1.92 | 99.77 | 352.67
1.93 | 99.94 | 350.95
1.94 | 100.12 | 349.29
1.95 | 100.29 | 347.55
1.96 | 100.46 | 345.88
1.97 | 100.63 | 344.23
1.98 | 100.79 | 342.59
1.99 | 100.96 | 340.97
2 | 101.13 | 339.36
2.01 | 101.3 | 337.77
2.02 | 101.46 | 336.19
2.03 | 101.63 | 334.63
2.04 | 101.79 | 333.09
2.05 | 101.96 | 331.56
2.06 | 102.12 | 330.04
2.07 | 102.28 | 328.54
2.08 | 102.44 | 327.05
2.09 | 102.6 | 325.58
2.1 | 102.76 | 324.12
2.11 | 102.92 | 322.67
2.12 | 103.08 | 321.23
2.13 | 103.24 | 319.81
2.14 | 103.4 | 318.4
2.15 | 103.56 | 317.01
2.16 | 103.71 | 315.63
2.17 | 103.87 | 314.26
2.18 | 104.02 | 312.9
2.19 | 104.18 | 311.55
2.2 | 104.33 | 310.22
2.21 | 104.48 | 308.9
2.22 | 104.64 | 307.59
2.23 | 104.79 | 306.29
2.24 | 107.94 | 305
2.25 | 105.09 | 303.72
2.26 | 105.24 | 302.46
2.27 | 105.39 | 301.2
2.28 | 105.54 | 299.96
2.29 | 105.69 | 298.72
2.3 | 105.84 | 297.5
2.31 | 105.99 | 296.29
2.32 | 106.13 | 295.08
2.33 | 106.28 | 293.89
2.34 | 106.43 | 292.71
2.35 | 106.57 | 291.53
2.36 | 106.72 | 290.37
2.37 | 106.86 | 289.22
2.38 | 107 | 288.07
2.39 | 107.15 | 286.94
2.4 | 107.29 | 285.81
2.41 | 107.43 | 284.69
2.42 | 107.57 | 283.59
2.43 | 107.72 | 282.49
2.44 | 107.86 | 281.4
2.45 | 108 | 280.32
2.46 | 108.14 | 279.24
2.47 | 108.28 | 278.18
2.48 | 108.42 | 277.12
2.49 | 108.55 | 276.07
2.5 | 108.69 | 275.03
2.51 | 108.83 | 274
2.52 | 108.97 | 272.98
2.53 | 109.1 | 271.96
2.54 | 109.24 | 270.96
2.55 | 109.37 | 269.95
2.56 | 109.51 | 268.96
2.57 | 109.64 | 267.98
2.58 | 109.78 | 267
2.59 | 109.91 | 266.03
2.6 | 110.04 | 265.06
2.61 | 110.18 | 264.11
2.62 | 110.31 | 263.16
2.63 | 110.44 | 262.22
2.64 | 110.57 | 261.28
2.65 | 110.7 | 260.35
2.68 | 110.84 | 259.43
2.67 | 110.97 | 258.52
2.68 | 111.1 | 257.61
2.69 | 111.22 | 256.71
2.7 | 111.35 | 255.81
2.71 | 111.48 | 254.92
2.72 | 111.61 | 254.04
2.73 | 111.74 | 253.17
2.74 | 111.87 | 252.3
2.75 | 111.97 | 251.43
2.76 | 112.12 | 250.58
2.77 | 112.25 | 249.72
2.78 | 112.37 | 248.88
2.79 | 112.5 | 248.04
2.8 | 112.62 | 247.21
2.81 | 112.75 | 246.38
2.82 | 112.87 | 245.56
2.83 | 112.99 | 244.74
2.84 | 113.12 | 243.93
2.85 | 113.24 | 243.12
2.86 | 113.36 | 242.32
2.87 | 113.49 | 241.53
2.88 | 113.61 | 240.74
2.89 | 113.73 | 239.95
2.9 | 113.85 | 239.18
2.91 | 113.97 | 238.4
2.92 | 114.09 | 237.63
2.93 | 114.21 | 236.87
2.94 | 114.33 | 236.11
2.95 | 114.45 | 235.36
2.96 | 114.57 | 234.61
2.97 | 114.69 | 233.87
2.98 | 114.81 | 233.13
2.99 | 114.93 | 232.4
3 | 115.04 | 231.67
3.01 | 115.16 | 230.94
3.02 | 115.28 | 230.22
3.03 | 115.4 | 229.51
3.04 | 115.51 | 228.8
3.05 | 115.63 | 228.09
3.06 | 115.74 | 227.39
3.07 | 115.86 | 226.69
3.08 | 115.98 | 226
3.09 | 116.09 | 225.31
3.1 | 116.2 | 224.63
3.11 | 116.32 | 223.95
3.12 | 116.43 | 223.27
3.13 | 116.55 | 222.6
3.14 | 116.66 | 221.94
3.15 | 116.77 | 221.27
3.16 | 116.89 | 220.61
3.17 | 117 | 219.96
3.18 | 117.11 | 219.31
3.19 | 117.22 | 218.66
3.2 | 117.33 | 218.02
3.21 | 117.44 | 217.38
3.22 | 117.55 | 216.74
3.23 | 117.67 | 216.11
3.24 | 117.78 | 215.49
3.25 | 117.89 | 214.86
3.26 | 118 | 214.24
3.27 | 118.1 | 213.63
3.28 | 118.21 | 213.01
3.29 | 118.32 | 212.4
3.3 | 118.43 | 211.8
3.31 | 118.54 | 211.2
3.32 | 118.65 | 210.6
3.33 | 118.75 | 210
3.34 | 118.86 | 209.41
3.35 | 118.97 | 208.82
3.36 | 119.08 | 208.24
3.37 | 119.18 | 207.66
3.38 | 119.29 | 207.08
3.39 | 119.4 | 206.51
3.4 | 119.5 | 205.93
3.41 | 119.61 | 205.37
3.42 | 119.71 | 204.8
3.43 | 119.82 | 204.24
3.44 | 119.92 | 203.68
3.45 | 120.03 | 203.13
3.46 | 120.13 | 202.57
3.47 | 120.23 | 202.03
3.48 | 120.34 | 201.48
3.49 | 120.44 | 200.94
3.5 | 120.54 | 200.4
3.51 | 120.65 | 199.96
3.52 | 120.75 | 199.93
3.53 | 120.85 | 198.79
3.54 | 120.95 | 198.27
3.55 | 121.06 | 197.74
3.56 | 121.16 | 197.22
3.57 | 121.26 | 196.7
3.58 | 121.36 | 196.18
3.59 | 121.46 | 195.67
3.6 | 121.56 | 195.16
3.61 | 121.66 | 194.65
3.62 | 121.76 | 194.14
3.63 | 121.86 | 193.64
3.64 | 121.96 | 193.14
3.65 | 122.06 | 192.64
3.66 | 122.16 | 192.15
3.67 | 122.26 | 191.66
3.68 | 122.36 | 191.17
3.69 | 122.46 | 190.68
3.7 | 122.56 | 190.19
3.71 | 122.65 | 189.71
3.72 | 122.75 | 189.23
3.73 | 122.85 | 188.76
3.74 | 122.95 | 188.28
3.75 | 123.04 | 187.81
3.76 | 123.14 | 187.34
3.77 | 123.24 | 186.87
3.78 | 123.34 | 186.41
3.79 | 123.43 | 185.94
3.8 | 123.53 | 185.48
3.81 | 123.62 | 185.03
3.82 | 123.72 | 184.57
3.83 | 123.81 | 184.12
3.84 | 123.91 | 183.67
3.85 | 124.01 | 183.22
3.86 | 124.1 | 182.77
3.87 | 124.19 | 182.33
3.88 | 124.29 | 181.89
3.89 | 124.38 | 181.45
3.9 | 124.48 | 181.01
3.91 | 124.57 | 180.57
3.92 | 124.66 | 180.14
3.93 | 124.76 | 179.91
3.94 | 124.85 | 179.23
3.95 | 124.94 | 178.86
3.96 | 125.04 | 178.43
3.97 | 125.13 | 178.01
3.98 | 125.22 | 177.59
3.99 | 125.31 | 177.17
4 | 125.41 | 176.75
4.01 | 125.5 | 176.34
4.02 | 125.59 | 175.93
4.03 | 125.68 | 175.52
4.04 | 125.77 | 175.11
4.05 | 125.86 | 174.7
4.06 | 125.95 | 174.3
4.07 | 126.04 | 173.89
4.08 | 126.14 | 173.49
4.09 | 126.23 | 173.09
4.1 | 126.32 | 172.7
4.11 | 126.41 | 172.3
4.12 | 126.5 | 171.91
4.13 | 126.58 | 171.52
4.14 | 126.67 | 171.13
4.15 | 126.76 | 170.74
4.16 | 126.85 | 170.36
4.17 | 126.94 | 169.97
4.18 | 127.03 | 169.59
4.19 | 127.12 | 169.21
4.2 | 127.21 | 168.83
4.21 | 127.29 | 168.45
4.22 | 127.38 | 168.08
4.23 | 127.47 | 167.71
4.24 | 127.56 | 167.33
4.25 | 127.64 | 166.96
4.26 | 127.73 | 166.6
4.27 | 127.82 | 166.23
4.28 | 127.91 | 165.86
4.29 | 127.99 | 165.5
4.3 | 128.08 | 165.14
4.31 | 128.16 | 164.78
4.32 | 128.25 | 164.42
4.33 | 128.34 | 164.06
4.34 | 128.42 | 163.71
4.35 | 128.51 | 163.35
4.36 | 128.59 | 163
4.37 | 128.68 | 162.65
4.38 | 128.76 | 162.3
4.39 | 128.85 | 161.96
4.4 | 128.93 | 161.61
4.41 | 129.02 | 161.26
4.42 | 129.1 | 160.92
4.43 | 129.19 | 160.58
4.44 | 129.27 | 160.24
4.45 | 129.36 | 159.9
4.46 | 129.44 | 159.57
4.47 | 129.52 | 159.23
4.48 | 129.61 | 158.9
4.49 | 129.69 | 158.56
4.5 | 129.77 | 158.23
4.51 | 129.86 | 157.9
4.52 | 129.94 | 157.57
4.53 | 130.02 | 157.25
4.54 | 130.1 | 156.92
4.55 | 130.19 | 156.6
4.56 | 130.27 | 156.28
4.57 | 130.35 | 155.95
4.58 | 130.43 | 155.63
4.59 | 130.51 | 155.32
4.6 | 130.6 | 155
4.61 | 130.68 | 154.68
4.62 | 130.76 | 154.37
4.63 | 130.84 | 154.05
4.64 | 130.92 | 153.74
4.65 | 131 | 153.43
4.66 | 131.08 | 153.12
4.67 | 131.16 | 152.81
4.68 | 131.24 | 152.51
4.69 | 131.32 | 152.2
4.7 | 131.4 | 151.9
4.71 | 131.48 | 151.6
4.72 | 131.56 | 151.29
4.73 | 131.64 | 150.99
4.74 | 131.72 | 150.69
4.75 | 131.8 | 150.4
4.76 | 131.88 | 150.1
4.77 | 131.96 | 149.8
4.78 | 132.04 | 149.51
4.79 | 132.12 | 149.22
4.8 | 132.2 | 148.92
4.81 | 132.28 | 148.63
4.82 | 132.35 | 148.34
4.83 | 132.43 | 148.05
4.84 | 132.51 | 147.77
4.85 | 132.59 | 147.48
4.86 | 132.67 | 147.2
4.87 | 132.74 | 146.91
4.88 | 132.82 | 146.63
4.89 | 132.9 | 146.35
4.9 | 132.98 | 146.07
4.91 | 133.05 | 145.79
4.92 | 133.13 | 145.51
4.93 | 133.21 | 145.23
4.94 | 133.28 | 144.96
4.95 | 133.36 | 144.68
4.96 | 133.44 | 144.41
4.97 | 133.51 | 144.13
4.98 | 133.59 | 143.86
4.99 | 133.67 | 143.59
5 | 133.74 | 143.32
5.1 | 134.5 | 140.68
5.2 | 135.24 | 138.14
5.3 | 135.96 | 135.69
5.4 | 136.68 | 133.33
5.5 | 137.39 | 131.05
5.6 | 138.08 | 128.85
5.7 | 138.77 | 126.73
5.8 | 139.44 | 124.68
5.9 | 140.1 | 122.69
6 | 140.76 | 120.77
6.1 | 141.4 | 118.91
6.2 | 142.04 | 117.11
6.3 | 142.67 | 115.36
6.4 | 143.29 | 113.67
6.5 | 143.9 | 112.03
6.6 | 144.5 | 110.44
6.7 | 145.1 | 108.89
6.8 | 145.69 | 107.38
6.9 | 146.27 | 105.92
7 | 146.84 | 104.5

## R1
1 | 2
TEMPERATURE CORRECTION FOR FRICTION LOSS IN TUBE
35 | 1.16
36 | 1.16
37 | 1.1559
38 | 1.1518
39 | 1.1476
40 | 1.1435
41 | 1.1394
42 | 1.1353
43 | 1.1312
44 | 1.1271
45 | 1.1229
46 | 1.1188
47 | 1.1147
48 | 1.1106
49 | 1.1065
50 | 1.1024
51 | 1.0982
52 | 1.0941
53 | 1.09
54 | 1.0859
55 | 1.0818
56 | 1.0776
57 | 1.0735
58 | 1.0694
59 | 1.0653
60 | 1.0612
61 | 1.0571
62 | 1.0529
63 | 1.0488
64 | 1.0447
65 | 1.0406
66 | 1.0365
67 | 1.0324
68 | 1.0282
69 | 1.0241
70 | 1.02
71 | 1.0174
72 | 1.0148
73 | 1.0122
74 | 1.0096
75 | 1.007
76 | 1.0044
77 | 1.0018
78 | 0.9992
79 | 0.9966 | Inlet Temp(T1) | 32
80 | 0.994 | Outlet Temp(T2) | 40
81 | 0.9914 | (T1-T2)/2 | 4 | °C
82 | 0.9888 |  | 39.2 | °F
83 | 0.9862 | R1 | 1.1476
84 | 0.9836
85 | 0.981
86 | 0.9784
87 | 0.9758
88 | 0.9732
89 | 0.9706
90 | 0.968
91 | 0.9659
92 | 0.9638
93 | 0.9617
94 | 0.9596
95 | 0.9575
96 | 0.9554
97 | 0.9533
98 | 0.9512
99 | 0.9491
100 | 0.947
101 | 0.9449
102 | 0.9428
103 | 0.9407
104 | 0.9386
105 | 0.9365
106 | 0.9344
107 | 0.9323
108 | 0.9302
109 | 0.9281
110 | 0.9265
111 | 0.925
112 | 0.924
113 | 0.923
114 | 0.92
115 | 0.9186
116 | 0.9173
117 | 0.916
118 | 0.9146
119 | 0.9133
120 | 0.912
121 | 0.911
122 | 0.9095
123 | 0.9085
124 | 0.908
125 | 0.9075
126 | 0.907
127 | 0.9065
128 | 0.906

## Re
| 1 | 2 | 3 |  | 1 | 2 | 3 |  | 1 | 2 | 3
ft/sec | A | B | C |  | A | B | C |  | A | B | C
2 | 0.08 | 0.08 | 0.02 | 2 | 0.16 | 0.08 | 0.04 | 2 | 0.24 | 0.06 | 0.04 | A = Tube end loss combined inlet and outlet
3 | 0.16 | 0.14 | 0.04 | 3 | 0.32 | 0.16 | 0.08 | 3 | 0.48 | 0.14 | 0.1 | B = Water box inlet loss
4 | 0.28 | 0.24 | 0.08 | 4 | 0.56 | 0.24 | 0.12 | 4 | 0.84 | 0.24 | 0.17 | C = Water box outlet loss
5 | 0.46 | 0.4 | 0.12 | 5 | 0.88 | 0.4 | 0.2 | 5 | 1.32 | 0.38 | 0.26
6 | 0.64 | 0.56 | 0.16 | 6 | 1.28 | 1.56 | 0.28 | 6 | 1.92 | 0.54 | 0.4
7 | 0.86 | 0.76 | 1.02 | 7 | 1.72 | 0.76 | 0.38 | 7 | 2.68 | 0.74 | 0.52
8 | 1.14 | 1 | 0.3 | 8 | 2.28 | 1 | 0.5 | 8 | 3.36 | 0.98 | 0.68
9 | 1.44 | 1.26 | 0.36 | 9 | 2.88 | 1.24 | 0.62 | 9 | 4.28 | 1.24 | 0.88
10 | 1.76 | 1.54 | 0.46 | 10 | 3.56 | 1.56 | 0.78 | 10 | 5.28 | 1.52 | 1.08
11 | 2.14 | 1.88 | 0.56 | 11 | 4.28 | 1.88 | 0.94 | 11 | 6.4 | 1.84 | 1.3
12 | 2.54 | 2.22 | 0.68 | 12 | 5.12 | 2.2 | 1.1 | 12 | 7.6 | 2.2 | 1.56
13 |  | 2.6 | 0.78 | 13 |  | 2.6 | 1.3 | 13 |  | 2.6 | 1.82
14 |  | 3.02 | 0.902 | 14 |  | 3.04 | 1.52 | 14 |  | 3 | 2.1
15 |  | 3.44 | 1.02 | 15 |  | 3.48 | 1.74 | 15 |  | 3.42 | 2.42
|  | No of pass |  |  | 2
|  | Water Velocity |  |  | 6 | ft/sec
|  | Tube End Loss |  |  | 0.64 | ft of water
| single pass | Water Box Inlet Loss |  |  | 0.56 | ft of water
|  | Water Box Outlet Loss |  |  | 0.16 | ft of water
|  | toatal loss |  |  | 1.36 | ft of water
|  | Tube End Loss |  |  | 1.28 | ft of water
| Double pass | Water Box Inlet Loss |  |  | 1.56 | ft of water
|  | Water Box Outlet Loss |  |  | 0.28 | ft of water
|  | toatal loss |  |  | 3.12 | ft of water
|  | Tube End Loss |  |  | 1.92 | ft of water
| Three pass | Water Box Inlet Loss |  |  | 0.54 | ft of water
|  | Water Box Outlet Loss |  |  | 0.4 | ft of water
|  | toatal loss |  |  | 2.86 | ft of water
|  | Water Box and Tube End Loss |  |  | 3.12 | ft of water